Network UPS Tools: Megatec Protocol information 
A. General: This document specifies the RS232C communication protocol of the Advance-Intelligent UPS. The protocol provided the following

            features :
         1. Monitor charger status.

         2. Monitor battery status and condition.

         3. Monitor the utility status.

         4. Provide the power switch function for computer to turn on and

            off the utility on schedule for power saving.
 Computer will control information exchange by a query followed by<cr>. UPS will respond with information followed by a <cr> or action.

B. Hardware:

            BAUD RATE............... : 2400 bps

            DATA LENGTH.......... : 8 bits

            STOP BIT..................... : 1 bit

            PARITY........................ : NONE
            CABLING :
               COMPUTER                  UPS

            ===================================

                  RX   <----------   TX  (pin 2)

                  TX    ---------->  RX  (pin 3)

                  GND  <----------   GND (pin 5)
                  (9 pins female D-type connector)
C. COMMUNICATION PROTOCOL:
1. Status Inquiry:
Computer : Q1<cr>

        UPS      : UPS status data stream, such as

             (MMM.M NNN.N PPP.P QQQ RR.R S.SS TT.T  b7b6b5b4b3b2b1b0<cr>
        UPS status data stream :


There should be a space character between every field for data


separation. The meaning of each field is list as followed:

     a. Start byte    : (

b.I/P voltage   : MMM.M

         M is and integer number ranging from 0 to 9.The unit is Volt.
     c.I/P fault voltage : NNN.N

             N is and integer number ranging from 0 to 9.

             The unit is Volt.
             ** For OFF LINE UPS**
           Its purpose is to identify a short duration voltage glitch

           which cause OFF line UPS to go to Invter mode. If this occurs

           input voltage will appear normal at query prior to glitch and

           will still appear normal at next query.

           The I/P fault voltage will hold glitch voltage till next

           query. After query, the I/P fault voltage will be same as I/P

           voltage until next glitch occurs.
                  ** For ON LINE UPS**

                Its purpose is to identify a short duration utility fail

           which cause ON line UPS to go to battery mode. If this occurs

           input voltage will appear normal at query prior to fail and

           will still appear normal at next query.

                The I/P fault voltage will hold utility fail voltage till

           next query. After query, the I/P voltage will be same as I/P

           voltage until next utility fail occurs.

      d.O/P voltage   : PPP.P

           P is an integer number ranging form 0 to 9.

The unit is Volt.

      e.O/P current   : QQQ

           QQQ is a percent of maximum current, not an absolute value.
      f.I/P frequency : RR.R

           R is an integer number ranging from 0 to 9.

           The unit is HZ.

      g.Battery voltage : SS.S or S.SS

           S is an integer number ranging from 0 to 9.

           For on-line units battery voltage/cell is provided in the

           form S.SS .

           For standby units actual battery voltage is provided in

           the form SS.S .

           UPS type in UPS status will determine which reading was

           obtained.

      h.Temperature   : TT.T

            T is an integer number ranging form 0 to 9.

            The unit is degree of centigrade.

       i.UPS Status    : <U>

             <U> is one byte of binary information such as

             <b7b6b5b4b3b2b1b0>.

 
Where bn is a ASCII character '0' or '1'.
UPS status :

Bit 
          Description
7    1  :  Utility Fail (Immediate)            


                    6    1  :  Battery Low                         


                    5    1  :  Bypass/Boost or Buck Active               

                    4    1  :  UPS Failed                          


                    3    1  :  UPS Type is Standby (0 is On_line)  


                    2    1  :  Test in Progress                    


 1    1  :  Shutdown Active                     


                    0    1  :  Beeper On                             

j.Stop Byte     : <cr>


Example: Computer : Q1<cr>


UPS      :

      (208.4 140.0 208.4 034 59.9 2.05 35.0 00110000<cr>
                  Means    : I/P voltage is 208.4V.

                             I/P fault voltage is 140.0V.

                             O/P voltage is 208.4V.

                             O/P current is 34 %.

                             I/P frequency is 59.9 HZ.

                             Battery voltage is 2.05V.

                             Temperature is 35.0 degrees of centigrade.

                             UPS type is on-line , UPS failed. Bypass

                             active , and shutdown not active.

2. Test for 10 seconds:

        Computer  : T<cr>

        UPS       : Test for 10 seconds and return to utility.

        If battery low occur during testing, UPS will return to

        utility immediately.

3.Test until battery low :

        Computer  : TL<cr>

        UPS       : Test until battery low and return to utility.

4.Test for specified time period :

        Computer  : T<n><cr>

        UPS       : Test for <n> minutes.

        a. During testing, UPS returns to utility immediately, if

           battery low occur.

        b. <n> is a number ranging from 01 to 99.

5. Turn On/Off beep -- Toggle the UPS beeper :

        Computer  : Q<cr>

        When the AC power failed, UPS will generate a warning beep to

        inform the manager. Manager could toggle the warning beep by

        sending this command .

6. Shutdown Command :

        Computer  : S<n><cr>

        UPS       : Shut UPS output off in <n> minutes.

      a. The UPS output will be off in <n> minutes, even if the

           utility power is present.

      b. If the battery low occurs before <n> minutes, the

           output is turned off immediately.

      c. After UPS shutdown, the controller of UPS monitors the

           utility power. If the utility is recovered, the UPS will wait

           for 10 seconds and connect the utility to output.

      d. <n> is a number ranging form .2, .3, ..., 01, 02, ..., up to 10.

        For example : S.3<cr> --- shut output off in (.3) minutes

7. Shutdown and Restore Command :

        Computer  : S<n>R<m><cr>

        UPS       : Shut UPS output off in <n> minutes, and waiting

                    for <m> minutes then turn on UPS output again.

      a. The shutdown sequence is the same as the previous command.

           When the <m> minutes expired, the utility do not restore,

           the UPS will wait until utility restore.

      b. If UPS is in shutdown waiting state, the "C" command can

           let the shutdown procedure cancelled.

      c. If UPS is in restore waiting state, the "C" command can

           let the UPS output turned on, but UPS must be hold off at

           least 10 seconds. (if utility is present)

      d. <n> is a number ranging form .2, .3, ..., 01, 02, ..., up to 10.

      e. <m> is a number ranging form 0001 to 9999.

8. Cancel Shutdown Command :

        Computer  : C<cr>

        UPS       : Cancel the SN<n><cr> and SN<n>R<m><cr> command.

        a. If UPS is in shut down waiting state, the shut down command

           is cancelled.

        b. If UPS is in restore waiting state, the UPS output is turned

           on, but UPS must be hold off at least 10 seconds.

           (if utility is present)

9. Cancel Test Command :

        Computer  : CT<cr>

        UPS       : Cancel all test activity and connect the utility to

                    output immediately.

10. UPS Information Command:



Computer
: I<cr>



UPS

: #Company_Name UPS_Model Version<cr>


This function will make the UPS respond with the basic information


about the company who manufacture the UPS, the model name of the


UPS and the version number of the UPS firmware. The length of


every field is listed as follows:

Company_Name
: 15 characters, leave space if less than 15 characters

UPS_Model
: 10 characters, leave space if less than 10 characters

Version

: 10 characters, leave space if less than 10 characters


There should be a space character between every field for separation.

11. UPS Rating Information:



Computer
: F<cr>



UPS


: #MMM.M QQQ SS.SS RR.R<cr>


This function makes the UPS answer the rating value of UPS. There


should be a space character between every field for


separation. The UPS's response contains the following information


field:



a. Rating Voltage
: MMM.M




b. Rating Current
: QQQ




c. Battery Voltage
: SS.SS or SSS.S




d. Frequency

: RR.R

D. COMMAND SUMMARY:

ITEM
COMMAND 
           DESCRIPTION              


 1a  
  D     
  Status Inquiry           *disable         


 1  
  Q1     
  Status Inquiry                    


 2  
  T     
  10 Seconds Test                   


 3  
  TL    
  Test until Battery Low            


 4  
  T<n>  
  Test for Specified Time Period    


 5  
  Q     
  Turn On/Off beep                  


 6  
  S<n>  
  Shut Down Command                 


 7  
S<n>R<m>
  Shut Down and Restore Command     


 8  
  C     
  Cancel Shut Down Command          


 9  
  CT    
  Cancel Test Command               


10
   I
  UPS Information Command


11
   F
  UPS Rating Information


E. Invalid Command/Information Handling

If the UPS receives any command that it could not handle, the UPS should

echo the received command back to the computer. The host should check if

the command send to UPS been echo or not. 

If there is any information field in the UPS's response which is

unavailable or not supported, the UPS should fill the field with '@'.
Notes by Russell Kroll, 4 April 2001: 

S01R0001 and S01R0002 may not work on early firmware versions. The failure mode is that the UPS turns off and never returns. The fix is to push the return value up by 2, i.e. S01R0003, and it will return online properly. 
